## Slide 1
CFD SIMULATIONS
FOR STERILIZATION PROCESS

## Slide 2
FOR STERILIZATION PROCESS
INTRODUCTION
One of the big challenges when you want:
to design a CS (clean steam) distribution system
to calculate the CS generator capacity
to configure a pressure regulator for a CS user point
is to evaluate the CS consumptions of the systems. Without having correct data, everything could go in wrong directions like:
to have an over-dimensioned CS generator, that will consume a lot of unnecessary energy
to have a pressure regulator that is not working properly, by having an outlet pressure bigger than the setpoint, and acting as a rudimentary on/off valve destroying frequently the valve seat.
CFD SIMULATIONS

## Slide 3
FOR STERILIZATION PROCESS
INTRODUCTION
A big mistake in most of the cases is to consider the system CS consumptions during the sterilization, to be the CS consumption given by the system producer. In most of the cases, this value is the maximum reached during the factory tests when the system is vacuumed, and the CS is penetrating the system.
The value given by the system producer could be 100x or 10x greater than the real one during the sterilization process.
CFD SIMULATIONS

## Slide 4
FOR STERILIZATION PROCESS
INTRODUCTION
Aseptconn offers to you Computational Fluid Dynamics (CFD) simulations services for the evaluation of the CS consumptions.
In the next slides we will present to you a case study for a 1000 liters tank.
CFD SIMULATIONS

## Slide 5
FOR STERILIZATION PROCESS
CASE STUDY – 1000 liters tank
CFD SIMULATIONS
We have considered a 1000 liters tank, placed into a clean room of 4.5 x 3.5 x 3 meters (L x W x H). The air is coming in with 20oC. The sterilization is done with steam at 121oC. The tank is jacketed in the middle region.
For this kind of tanks, the system producers could specify the CS consumption to be in the range 50÷100 kg/h !!!

## Slide 6: CFD SIMULATIONS
FOR STERILIZATION PROCESS
Calcualtion of the CS consumption during sterilization process, for 1000 liters vessel:
Air inlet velocity: 0.1 m/s
Air inlet velocity: 0.5 m/s
Steam consumption
during sterilization:
2.13 kg/h
Steam consumption
during sterilization:
0.82 kg/h

## Slide 7
FOR STERILIZATION PROCESS
CONCLUSIONS
CFD SIMULATIONS
It is very important to evaluate the CS consumptions during the sterilization phase. In most of the cases the values indicated by the producer could be 100x greater.
The consumptions are depending on a lot of parameters. With CFD simulations we can do very good evaluations for different conditions.
100X DIFFERENCE
REALLY COUNTS FOR YOUR PROJECT !!!